## COVER
VOLTAGE SCHEDULES 2022 Effective January 14th, 2022 The times for changes are according to BPA Timetable to help coordinate voltage schedules on the entire NW transmission system. NOTES: These voltage schedules do not supersede Dispatch Standing Orders or Study Limits Information Memos. The voltage schedule is a guide of preferred operating voltages and the associated alarms allowing dispatchers the ability to control voltage prior to any automatic actions. The described voltage set point and/or band is needed for voltage support and is incorporated into system studies. These voltage set points and/or bands are not System Voltage Limit SOLs. These voltage schedules are not voltage droop settings, they may be used as a starting point for voltage droop settings. The voltage schedule is written for the purpose of normal day to day voltage coordination. The appropriate Transmission Dispatcher can require deviations from this printed schedule as conditions on the grid require it. Attention GOP's: The generator voltage schedule assumes that the Generator Operator will follow the schedule while on-line and synchronized to the grid. GOP Notifications to BPA (TOP) when voltage schedule is not being maintained: 1. If the Generator Operator has an Large or Small Generator Interconnection Agreement (LGIA/SGIA) with BPA that specifies a power factor, and that power factor can not be provided, call BPA Dispatch. 2. If the Generator Operator does not have an LGIA/SGIA with BPA that specifies a power factor, and the generating facility reactive capability is not being fully utilized, call BPA Dispatch. VAR-002-4.1, Requirement 1 footnotes #1 and #2: [1] Start-up is deemed to have ended when the generator is ramped up to its minimum continuously sustainable load and the generator is prepared for continuous operation. [2] Shutdown is deemed to begin when the generator is ramped down to its minimum continuously sustainable load and the generator is prepared to go offline. For distributed generation the threshold for start-up and shutdown should be considered at 20% of the plant total capability or as specified in LGIA/SGIA. FOR QUESTION OR COMMENTS: James Wong (509) 822-4638 Email: jxwong@bpa.gov Audrey Stevenson (509) 319-3715 Email: acstevenson@bpa.gov

## USER GUIDE
USER GUIDE
Examples:
Plant | BUS KV | TARGET | HI |  | MED | LOW |  | BAND (+/- kV) | REFERENCE VOLTAGE | DATE | REMARKS
Plant X | 115 | 117 | 117 |  | 117 | 117 |  | 3 | Station X
Plant | BUS KV | TARGET | HI |  | MED | LOW |  | BAND (+/- kV) | REFERENCE VOLTAGE | DATE | REMARKS
Plant X | 115 |  | 118 |  | 117 | 116 |  | 3 | Station X
Plant | BUS KV | TARGET | HI |  | MED | LOW |  | BAND (+/- kV) | REFERENCE VOLTAGE | DATE | REMARKS
Plant X | 115 | 117 | 119 | MAX |  | 116 | MIN | 3 | Station X
Definitions: BUS KV: Nominal kV TARGET: Sub schedules: Voltage set point that dispatch targets by utilizing their reactive devices to control voltage. Gen Schedules: Voltage set point that the plant uses to control the Reference Voltage. HI- MED-LOW: Time of day Target or range (Max/Min) that is applied to a non time of day Target. The range is a “tolerance band”, not a control dead-band in the generator’s excitation system (see examples below). BAND (+/-kV): Allowed band applied to time of day Target or range. The Band is a “tolerance band”, not a control dead-band in the generator’s excitation system (see examples below). Required value in VAR-001-4 revision. REFERENCE VOLTAGE: Point where plant is referencing voltage to control to the Target. REMARKS: Internal or external notes for that plant. TIMETABLE: Sheet in voltage schedule file, that provides days and times for when HI-MED-LOW Targets should be used.
Flat Schedule: Target is not adjusted throughout the day.
In the example above, Plant X would set their Target to 117kV for Station X. The band of +/-3kV, allows the station voltage to vary +/-3kV from the flat Target due to system conditions. Station X's voltage schedule varies from 120kV to 114kV with Plant X's Target set to 117kV.
Time of Day Schedule: Target is adjusted throughout the day according to Timetable.
In the example above, Plant X would set their Target to 118kV, 117kV, or 116kV (HI, MED, or LOW respectively) depending on the time of day (see Timetable) for Station X. The band of +/- 3kV, allows the station to vary +/- 3kV from the applicable Target due to system conditions. Station X's voltage schedule during HI varies from 121kV to 115kV with Plant X's Target set to 118kV.
In the example above, Plant X would set their Target to 117kV for Station X. The Max and Min is the voltage range around the Target. The band allowance of +/-3kV, allows the station to vary +/-3kV from the Max and Min due to system conditions. Station X's voltage schedule varies from 122kV to 113kV with Plant X's Target set to 117kV.
Range with Target Schedule: Target and range are not adjusted throughout the day.

## TIMETABLE
TIMETABLES
The timetables below are used in conjunction with the following tabs for sub schedules and gen schedules.
These provide the time of day for each system loading level (HI, MED, LOW).
IDAHO-UTAH-MONTANA AREA (MST or MAST, prevailing)
| Medium |  | High | Medium | Low
| 630 |  | 730 | 2200 | 2330
Weekdays | to |  | to | to | to
| 730 |  | 2200 | 2330 | 630
(0700 SAT.) (0830)**
| 700 |  | 800 | 2200 | 2330
Saturdays | to |  | to | to | to
| 800 |  | 2200 | 2330 | 830
Sunday
Sundays | 830 |  | 1730 | 2030 | 2230
and | to |  | to | to | to
Holidays ** | 1730 |  | 2030 | 2230 | 630
Monday
OREGON-WASHINGTON-BRITISH COLUMBIA AREA (PST or PAST, prevailing)
| Medium |  | High | Medium | Low
| 600 |  | 700 | 2130 | 2400
Weekdays | to |  | to | to | to
| 700 |  | 2130 | 2400 | 600
(0700 SAT.) (0800)**
| 700 |  | 800 | 2130 | 2330
Saturdays | to |  | to | to | to
| 800 |  | 2130 | 2330 | 800
Sunday
Sundays | 800 |  | 1000 | 2030 | 2300
and | to |  | to | to | to
Holidays ** | 1000 |  | 2030 | 2300 | 600
Monday
** Holidays: New Year's Day, Memorial Day, Independence Day, Labor Day, Thanksgiving Day, Christmas Day

## HOLIDAYS
HOLIDAYS FOR VOLTAGE CONTROL
2022
EVENT | DATE | DAY OF WEEK
NEW YEAR'S DAY 2022 | 2022-01-01 | Saturday
MEMORIAL DAY | 2022-05-30 | Monday
INDEPENDANCE DAY | 2022-07-04 | Monday
LABOR DAY | 2022-09-05 | Monday
THANKSGIVING DAY | 2022-11-24 | Thursday
CHRISTMAS DAY | 2022-12-25 | Sunday
NEW YEAR'S DAY 2023 | 2023-01-01 | Sunday

## SUB SCHEDULES
SUBSTATION SCHEDULES
STATION | BUS KV | TARGET | HI |  | MED | LOW |  | BAND (+/- kV) | REMARKS | TOP Interface | DATE | SCADA ID
ABERDEEN | 115 |  | 118 |  | 117 | 116 |  | +3.0/-2.0 |  |  | 1992-02-01 | ABERDEEN
ADDY | 115 |  | 117 |  | 117 | 117 |  | +2.0/-2.0 | 117kV based on system voltage studies | Avista | 2001-03-01 | ADDY
ADDY | 230 | 235 | 240 | MAX |  | 230 | MIN |  |  |  | 1982-02-01 | ADDY
ALBANY | 115 |  | 119 |  | 118 | 117 |  | +2.0/-2.0 |  | PAC | 1992-02-01 | ALBANY
ALCOA | 115 | 118 | 121 | MAX |  | 115 | MIN |  |  | CCPUD | 1991-02-01 | ALCOA
ALLSTON | 115 |  | 117 |  | 116 | 115 |  | +4.0/-1.0 |  | PGE | 2000-03-01 | ALLSTON
ALLSTON | 230 |  | 239 |  | 237 | 236 |  | +3.0/-3.0 | 234kV MINIMUM | PGE | 1976-01-01 | ALLSTON
ALLSTON | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  |  | 1988-02-01 | ALLSTON
ALVEY | 115 |  | 120 |  | 119 | 118 |  | +4.0/-3.0 |  | EWEB, PAC | 1992-02-01 | ALVEY
ALVEY | 230 |  | 239 |  | 236 | 234 |  | +3.0/-3.0 |  | PAC | 1992-02-01 | ALVEY
ALVEY | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  | PAC | 1994-02-01 | ALVEY
ANACONDA | 115 |  | 119 |  | 119 | 119 |  | +4.0/-3.0 | COORD. W/NWE DISPATCHER | NWE | 1987-10-01 | ANACONDA
ANACONDA | 230 | 236 | 242 | MAX |  | 230 | MIN |  | COORD. W/NWE DISPATCHER | NWE | 1991-02-01 | ANACONDA
ASHE | 500 | 540 | 550 | MAX |  | 528 | MIN |  | CGS |  | 2020-05-20 | ASHE
ASHE | 230 | 239.5 | 242 | MAX |  | 237 | MIN |  | 237kV MINIMUM |  | 2020-05-14 | ASHE
for CGS(WNP#2) SS support
BADGER CANYON | 115 |  | 120 |  | 119 | 118 |  | +2.0/-2.0 | SUMMER (MAY-SEPT) |  | 1987-02-01 | BADGER_C
BADGER CANYON | 115 |  | 119 |  | 118 | 117 |  | +2.0/-2.0 | WINTER (OCT-APRIL) |  | 1988-02-01 | BADGER CANYON
BANDON | 115 |  | 119 |  | 118 | 117 |  | +2.0/-3.0 |  |  | 1992-02-01 | BANDON
BELL | 115 |  | 115 |  | 115 | 115 |  | +3.0/-3.0 | Flat schedule at Bell | Avista | 2005-11-05 | BELL
BELL | 230 |  | 238 |  | 238 | 238 |  | +3.0/-3.0 | Change for year round operation | Avista | 2008-03-08 | BELL
BELL | 500 | 540 | 550 | MAX |  | 520 | MIN |  |  |  | 1991-02-01 | BELL
BELLINGHAM | 115 |  | 116 |  | 116 | 116 |  | +1.0/-0.6 | Request by PSE for flat schedule | PSE | 2003-03-03 | BELLNGHM
to reduce loop Vars with Portal Way
BELLINGHAM | 230 | 238 | 240 | MAX |  | 235 | MIN |  |  | PSE | 2005-12-05 | BELLNGHM
BENTON | 115 |  | 119 |  | 119 | 119 |  | +2.0/-2.0 | SUMMER (MAY-SEPT) |  | 2017-12-17 | BENTON
BENTON | 115 |  | 118 |  | 118 | 118 |  | +2.0/-1.0 | WINTER (OCT-APRIL) |  | 2017-12-17 | BENTON
BENTON | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1986-03-01 | BENTON
BIG EDDY | 115 |  | 120 |  | 119 | 118 |  | +3.0/-2.0 |  |  | 1992-02-01 | BIG_EDDY
BIG EDDY | 230 |  | 240 |  | 239 | 237 |  | +3.0/-2.0 |  |  | 1999-02-01 | BIG_EDDY
BIG EDDY | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  |  | 1990-02-01 | BIG_EDDY
BOARDMAN | 69 | 70.5 | 72 | MAX |  | 69 | MIN |  |  |  | 1991-02-01 | BOARDMAN
BOARDMAN | 115 | 118 | 121 | MAX |  | 115 | MIN |  |  |  | 2020-11-20 | BOARDMAN
BONNERS FERRY | 115 |  | 117 |  | 117 | 117 |  | +2.0/-2.0 |  | Avista | 2021-02-21 | BONR_FRY
BOUNDARY | 115 | 118 | 121 | MAX |  | 115 | MIN |  |  |  | 2020-11-20 | BOUNDARY
BOUNDARY | 230 |  | 240 |  | 240 | 240 |  | +2.0/-2.0 |  | BCTC, SCL | 2018-07-01 | BOUNDARY
BRIDGE | 138 | 140.5 | 145 | MAX |  | 136 | MIN |  |  |  | 2000-03-01 | BRIDGE
BUCKLEY | 500 | 542.5 | 550 | MAX |  | 535 | MIN |  |  |  | 2004-12-04 | BUCKLEY
CAPTAIN JACK | 500 | 542.5 | 550 | MAX |  | 535 | MIN |  | KEEP VOLTAGES HIGH | WAPA | 2004-12-04 | CAPTJACK
DURING HEAVY TRANSFERS
CARDWELL | 115 |  | 117 |  | 116 | 115 |  | +3.0/-2.0 |  | PAC | 1991-02-01 | CARDWELL
CARLTON | 115 |  | 118 |  | 117 | 116 |  | +2.0/-2.0 |  | PGE | 1992-02-01 | CARLTON
CARLTON | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1980-01-01 | CARLTON
CENTRAL FERRY | 230 | 238 | 242 | MAX |  | 234 | MIN |  |  |  |  | CENTFERY
CENTRAL FERRY | 500 | 542.5 | 550 | MAX |  | 535 | MIN |  |  |  | 2012-12-22 | CENTFERY
CHEHALIS | 69 |  | 69 |  | 68.5 | 68 |  | +2.0/-2.0 |  |  | 1992-02-01 | CHEHALIS
CHEHALIS | 115 |  | 118 |  | 117 | 116 |  | +3.0/-2.0 |  |  | 1992-02-01 | CHEHALIS
CHEHALIS | 230 |  | 239 |  | 237 | 235 |  | +3.0/-3.0 |  | TPWR | 1980-01-01 | CHEHALIS
CHEMAWA | 57 | 59.9 | 61 | MAX |  | 58.8 | MIN |  |  |  | 1980-01-01 | CHEMAWA
CHEMAWA | 115 |  | 119 |  | 118 | 117 |  | +2.0/-3.0 |  | PGE | 1992-02-01 | CHEMAWA
CHEMAWA | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1980-01-01 | CHEMAWA
CHENOWETH | 115 |  | 120 |  | 119 | 118 |  | +2.0/-4.0 |  |  | 1988-02-01 | CHENOWTH
CHIEF JOSEPH | 230 |  | 240 |  | 238 | 236 |  | +2.0/-2.0 |  |  | 2000-03-01 | CHIEF_JO
CHIEF JOSEPH | 500 | 539 | 550 | MAX |  | 535 | MIN |  |  |  | 2016-03-01 | CHIEF_JO
COLUMBIA | 115 |  | 119 |  | 118 | 117 |  | +3.0/-3.0 |  | CHPUD, GCPUD | 1993-02-01 | COLUMBIA
COLUMBIA | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  | CHPUD, GCPUD | 1984-05-01 | COLUMBIA
COLUMBIA FALLS | 115 |  | 118 |  | 117 | 116 |  | +2.0/-2.0 |  |  | 1992-02-01 | COL_FALS
COLUMBIA FALLS | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1989-05-01 | COL_FALS
COLVILLE | 115 |  | 118 |  | 118 | 118 |  | +2.0/-2.0 |  |  | 2018-07-01 | COLVILLE
CONKELLEY | 230 |  | 242 | MAX |  | 232 | MIN |  | MST |  | 2017-12-01 | CONKELLY
COSMOPOLIS | 115 |  | 118 |  | 117 | 116 |  | +2.0/-2.0 |  |  | 1992-02-01 | COSMOPLS
COVINGTON | 230 | 238 | 240 | MAX |  | 235 | MIN |  |  | PSE, SCL | 2005-12-05 | COVINGTN
COWLITZ | 115 |  | 117 |  | 116 | 115 |  | +2.0/-2.0 |  |  | 1991-02-01 | COWLITZ
COYOTE SPRINGS | 500 | 542 | 550 | MAX |  | 535 | MIN |  |  | Avista, PGE | 2018-07-01 | COYOTE_S
CUSICK | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 2000-03-01 | CUSICK
CUSTER | 230 |  | 239 |  | 237 | 235 |  | +2.0/-2.0 |  | PSE | 1979-03-01 | CUSTER
CUSTER | 500 | 527.5 | 540 | MAX |  | 515 | MIN |  | COORD. WITH BCH | BCTC | 1984-01-01 | CUSTER
DRISCOLL | 230 | 237.5 | 242 | MAX |  | 233 | MIN |  |  |  | 1994-02-01 | DRISCOLL
DRUMMOND | 46 | 47.15 | 48.3 | MAX |  | 46 | MIN |  |  |  | 1993-03-01 | DRUMMOND
DRUMMOND | 115 | 118 | 121 | MAX |  | 115 | MIN |  |  |  | 1988-02-01 | DRUMMOND
EAST OMAK | 115 |  | 119 |  | 118 | 117 |  | +2.0/-2.0 |  | DCPUD | 1992-02-01 | EASTOMAK
EAST OMAK | 230 | 235 | 240 | MAX |  | 230 | MIN |  |  |  | 1982-02-01 | EASTOMAK
ECHO LAKE | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  |  | 1994-02-01 | ECHOLAKE
ELLENSBURG | 115 |  | 119 |  | 118 | 117 |  | +3.0/-3.0 |  |  | 2021-02-21 | ELENSBRG
EUGENE | 69 | 67.5 | 68 | MAX |  | 67 | MIN |  |  | EWEB | 1980-01-01 | EUGENE
EUGENE | 115 |  | 120 |  | 119 | 118 |  | +1.0/-6.0 |  |  | 1992-02-01 | EUGENE
FAIRMOUNT | 115 | 118 | 120 | MAX |  | 112 | MIN |  | Var Coord with Shelton/Oly |  | 2005-03-05 | FAIRMONT
FAIRMOUNT | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  | PAC | 1991-02-01 | FAIRMONT
FAIRVIEW | 115 |  | 119 |  | 118 | 117 |  | +2.0/-2.0 |  | PAC | 1992-02-01 | FAIRVIEW
FAIRVIEW | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1980-01-01 | FAIRVIEW
FLATHEAD | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1991-02-01 | FLATHEAD
FOREST GROVE | 115 |  | 118 |  | 117 | 116 |  | +2.0/-2.0 |  |  | 1992-02-01 | FOR_GROV
FRANKLIN | 115 |  | 120 |  | 119 | 118 |  | +2.0/-2.0 | SUMMER (MAY-SEPT) |  | 1988-02-01 | FRANKLIN
FRANKLIN | 115 |  | 119 |  | 118 | 117 |  | +2.0/-2.0 | WINTER (OCT-APR) | NWE | 1988-02-01 | FRANKLIN
GARRISON | 230 | 237 | 240 | MAX |  | 230 | MIN |  | COORD. W/NWE DISPATCHER | NWE | 1990-05-01 | GARRISON
GARRISON | 500 | 542.5 | 550 | MAX |  | 535 | MIN |  | COORD. W/NWE DISPATCHER |  | 2004-12-04 | GARRISON
GOSHEN | 115 | 118 | 121 | MAX |  | 115 | MIN |  |  |  | 1988-02-01 | GOSHEN
GOSHEN | 161 | 165 | 169 | MAX |  | 161 | MIN |  |  | PAC | 1988-02-01 | GOSHEN
GRANDVIEW | 115 |  | 119 |  | 118 | 117 |  | +2.0/-2.0 |  | PGE | 1987-02-01 | GRANDVEW
GRIZZLY | 500 | 542.5 | 550 | MAX |  | 535 | MIN |  | KEEP VOLTAGES HIGH |  | 2004-12-04 | GRIZZLY
DURING HEAVY TRANSFERS
HANFORD | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  |  | 1994-02-01 | HANFORD
HAPPY VALLEY | 115 | 118 | 120 | MAX |  | 112 | MIN |  |  |  | 2005-03-05 | HAPPYVLY
HAPPY VALLEY | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  | IPC | 1985-09-01 | HAPPYVLY
HARNEY | 115 | 118 | 121 | MAX |  | 114 | MIN |  |  |  | 1984-09-01 | HARNEY
HARVALUM | 230 | 239 | 242 | MAX |  | 236 | MIN |  |  | Avista | 2009-12-09 | HARVALUM
HATWAI | 230 | 236.5 | 239 | MAX |  | 234 | MIN |  |  |  | 1991-02-01 | HATWAI
HATWAI | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  |  | 1992-02-01 | HATWAI
HEYBURN | 138 | 140.5 | 145 | MAX |  | 136 | MIN |  |  |  | 2000-03-01 | HEYBURN
HILLTOP | 230 | 238 | 242 | MAX |  | 234 | MIN |  |  |  | 2012-06-12 | HILLTOP
HOLCOMB | 115 |  | 118 |  | 117 | 116 |  | +4.0/-4.0 |  | PAC | 1992-02-01 | HOLCOMB
HOOD RIVER | 115 |  | 120 |  | 119 | 118 |  | +2.0/-3.0 |  |  | 1992-02-01 | HOOD_RVR
HORSE HEAVEN | 115 |  | 119 |  | 119 | 119 |  | +2.0/-2.0 | SUMMER (MAY-SEPT) request by BCPUD |  | 2017-12-17 | HORSE_HV
HORSE HEAVEN | 115 |  | 118 |  | 118 | 118 |  | +2.0/-2.0 | WINTER (OCT-APRIL) request by BCPUD |  | 2017-12-17 | HORSE_HV
HORSE HEAVEN | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  | Avista, NWE | 1979-11-01 | HORSE_HV
HOT SPRINGS | 230 | 235 | 240 | MAX |  | 230 | MIN |  | COORD. WITH AVA AND NWE |  | 1990-05-01 | HOT_SPRG
HOT SPRINGS | 500 | 540 | 550 | MAX |  | 530 | MIN |  | MST (SEE DSO 319) |  | 2020-11-20 | HOT_SPRG
INTALCO | 230 |  | 239 |  | 237 | 235 |  | +2.0/-2.0 |  |  | 1980-01-01 | INTALCO
JOHN DAY | 230 | 239.5 | 242 | MAX |  | 237 | MIN |  |  |  | 2013-12-13 | JOHN_DAY
JOHN DAY | 500 |  | 542 |  | 540 | 540 |  | +2.0/-2.0 | change HI schedule for RR & area voltage | NWE | 2008-09-08 | JOHN_DAY
KALISPEL | 115 |  | 118 |  | 117 | 116 |  | +2.0/-6.0 |  | PGE | 1992-02-01 | KALISPEL
KEELER | 115 |  | 118 |  | 117 | 116 |  | +3.0/-2.0 |  | PGE | 1992-02-01 | KEELER
KEELER | 230 |  | 240 |  | 238 | 236 |  | +4.0/-4.0 |  |  | 1992-02-01 | KEELER
KEELER | 500 | 540 | 550 | MAX |  | 530 | MIN |  | SEE DSO #324 |  | 1988-02-01 | KEELER
KITSAP | 115 |  | 118 |  | 118 | 118 |  | +2.0/-2.0 | to control loop VARs with OLY |  | 2003-03-03 | KITSAP
KITSAP | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1980-01-01 | KITSAP
LAGRANDE | 69 | 70 | 71.5 | MAX |  | 68.5 | MIN |  |  | IPC | 1980-01-01 | LAGRANDE
LAGRANDE | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1978-01-01 | LAGRANDE
LANCASTER | 230 | 239.5 | 241 | MAX |  | 238 | MIN |  | Change for year round operation | EWEB | 2007-10-07 | LANCASTR
LANE | 115 |  | 120 |  | 119 | 118 |  | +4.0/-2.0 |  |  | 1992-02-01 | LANE
LANE | 230 |  | 239 |  | 236 | 234 |  | +2.0/-2.0 |  |  | 1992-02-01 | LANE
LANE | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  | PAC | 1988-02-01 | LANE
LAPINE | 115 |  | 119 |  | 118 | 117 |  | +1.0/-3.0 |  | PAC | 1988-02-01 | LA_PINE
LAPINE | 230 | 235 | 240 | MAX |  | 230 | MIN |  |  | PAC | 1988-02-01 | LA_PINE
LEXINGTON | 115 |  | 117 |  | 116 | 115 |  | +2.0/-2.0 |  | PAC | 1991-02-01 | LEXINGTN
LEXINGTON | 230 |  | 238 |  | 236 | 234 |  | +2.0/-2.0 |  |  | 1991-02-01 | LEXINGTN
LIBBY | 115 |  | 117 |  | 116 | 115 |  | +2.0/-2.0 | MST |  | 1992-02-01 | LIBBY
LONGVIEW | 69 | 69.5 | 70.5 | MAX |  | 68.5 | MIN |  |  |  | 1980-01-01 | LONGVIEW
LONGVIEW | 115 |  | 117 |  | 116 | 115 |  | +2.0/-2.0 |  |  | 1991-02-01 | LONGVIEW
LONGVIEW | 230 |  | 238 |  | 236 | 234 |  | +3.0/-2.0 |  |  | 1991-02-01 | LONGVIEW
LOOKOUT POINT | 115 |  | 121 |  | 119 | 118 |  | +3.0/-3.0 |  |  | 1992-02-01 | LOOKOTPT
LOST RIVER | 69 | 71 | 73 | MAX |  | 69 | MIN |  |  |  | 1988-02-01 | LOST_RVR
LOST RIVER | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1988-02-01 | LOST_RVR
MACKS INN | 46 | 47 | 48.3 | MAX |  | 46 | MIN |  |  |  | 1995-03-01 | MACKSINN
MACKS INN | 115 | 119 | 121 | MAX |  | 115 | MIN |  |  | PAC, PG&E | 1995-03-01 | MACKSINN
MALIN | 500 | 542.5 | 550 | MAX |  | 535 | MIN |  | KEEP VOLTAGES HIGH |  | 2004-12-04 | MALIN
[9 empty] | DURING HEAVY TRANSFERS | PSE, SCL
MAPLE VALLEY | 230 | 238 | 240 | MAX |  | 235 | MIN |  |  |  | 2005-12-05 | MAPLE_VL
MARION | 500 | 540 | 550 | MAX |  | 530 | MIN |  | SEE DSO #324 | PAC | 1994-02-01 | MARION
MARTIN CREEK | 115 |  | 120 |  | 119 | 118 |  | +3.0/-2.0 |  | PAC | 1992-02-01 | MARTIN_C
MARTIN CREEK | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  | PGE | 1980-01-01 | MARTIN CREEK
MCMINNVILLE | 115 |  | 118 |  | 117 | 116 |  | +3.0/-4.0 |  | PAC | 1992-02-01 | MCMINVIL
MCNARY | 69 | 70.25 | 71.5 | MAX |  | 69 | MIN |  |  | PAC | 1956-01-01 | MCNARY
MCNARY | 115 |  | 120 |  | 119 | 118 |  | +3.0/-3.0 | SUMMER (MAY-SEPT) |  | 1979-01-01 | MCNARY
MCNARY | 115 |  | 119 |  | 118 | 117 |  | +3.0/-3.0 | WINTER (OCT-APRIL) | PGE | 1988-02-01 | MCNARY
MCNARY | 230 |  | 242 |  | 240 | 238 |  | +3.0/-4.0 | SUMMER (MAY-SEP) |  | 1993-03-01 | MCNARY
MCNARY | 230 |  | 240 |  | 239 | 238 |  | +3.0/-4.0 | WINTER (OCT-APRIL) | PAC | 2009-04-09 | MCNARY
MCNARY | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  | PAC | 1994-02-01 | MCNARY
MIDWAY | 115 |  | 120 |  | 119 | 118 |  | +3.0/-4.0 | SUMMER (MAY-SEPT) |  | 1981-01-01 | MIDWAY
MIDWAY | 115 |  | 119 |  | 118 | 117 |  | +3.0/-4.0 | WINTER (OCT-APRIL) | GCPUD, PAC | 1988-02-01 | MIDWAY
MIDWAY | 230 |  | 239 |  | 239 | 239 |  | +4.0/-2.0 | 239 kV FLAT SCHEDULE to coordinate with |  | 2016-03-01 | MIDWAY
[9 empty] | Grant PUD Priest Rapids voltage schedule | PSE
MONROE | 230 | 238 | 240 | MAX |  | 235 | MIN |  |  |  | 2005-12-05 | MONROE
MONROE | 500 | 537.5 | 550 | MAX |  | 525 | MIN |  | SEE DSO #322 | PAC | 1994-02-01 | MONROE
MORROW FLAT | 230 | 240 | 242 | MAX |  | 235 | MIN |  |  |  |  | MORWFLAT
MORROW FLAT | 115 |  | 118 |  | 118 | 118 |  | +2.0/-2.0 |  |  |  | MORWFLAT
MOXEE | 115 |  | 119 |  | 118 | 117 |  | +2.0/-2.0 |  | PSE, SCPUD | 1988-02-01 | MOXEE
MURRAY | 115 |  | 115 |  | 114 | 113 |  | +2.0/-2.0 |  | PSE | 1992-02-01 | MURRAY
MURRAY | 230 | 238 | 240 | MAX |  | 235 | MIN |  |  |  | 2005-12-05 | MURRAY
NAPAVINE | 500 | 537.5 | 550 | MAX |  | 525 | MIN |  | see Chehalis Power |  | 2002-03-02 | NAPAVINE
NASELLE | 115 |  | 118 |  | 117 | 116 |  | +2.0/-3.0 |  |  | 1992-02-01 | NASELLE
N. BONNEVILLE | 230 |  | 239 |  | 236 | 234 |  | +4.0/-3.0 |  | PSE | 1978-08-01 | N_BONNVL
OLYMPIA | 115 |  | 118 |  | 118 | 118 |  | +5.0/-1.0 | request by PSE for flat schedule |  | 2003-03-03 | OLYMPIA
to coord loop Var flows w/Tono
OLYMPIA | 230 |  | 239 |  | 237 | 235 |  | +4.0/-4.0 |  |  | 1992-02-01 | OLYMPIA
OREGON CITY | 57 | 60.75 | 62.5 | MAX |  | 59 | MIN |  |  | PGE | 1977-01-01 | ORE_CITY
OREGON CITY | 115 |  | 118 |  | 117 | 116 |  | +2.0/-2.0 |  |  | 1992-02-01 | ORE_CITY
OSTRANDER | 500 | 540 | 550 | MAX |  | 530 | MIN |  | SEE DSO #324 |  | 1987-02-01 | OSTRNDER
PAUL | 500 | 537.5 | 550 | MAX |  | 525 | MIN |  |  | PGE | 1994-02-01 | PAUL
PEARL | 230 |  | 240 |  | 238 | 236 |  | +2.0/-3.0 |  |  | 1981-01-01 | PEARL
PEARL 500 | 500 | 540 | 550 | MAX |  | 530 | MIN |  | SEE DSO #324 | PAC | 1991-02-01 | PEARL
PONDEROSA | 230 | 236 | 242 | MAX |  | 230 | MIN |  | (COORD W/PP&L) | PAC | 1993-03-01 | PONDROSA
PONDEROSA | 500 | 535 | 550 | MAX |  | 520 | MIN |  |  |  | 1986-11-01 | PONDROSA
PORT ANGELES | 69 |  | 69 |  | 69 | 69 |  | +2.0/-2.0 | Customer Request via Region |  | 2003-04-03 | PORT_ANG
PORT ANGELES | 115 | 115 | 120 | MAX |  | 112 | MIN |  |  |  | 2005-03-05 | PORT_ANG
QUENETT CREEK | 230 | 238 | 242 | MAX |  | 235 | MIN |  |  |  | 2021-12-21 | QUENETT
RAVER | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  |  | 1994-02-01 | RAVER
RAVER | 230 | 238 | 240 | MAX |  | 235 | MIN |  |  |  | 2022-01-01 | RAVER
RAYMOND | 115 |  | 118 |  | 117 | 116 |  | +3.0/-2.0 |  | PAC | 1992-02-01 | RAYMOND
REDMOND | 69 | 69.5 | 72 | MAX |  | 67 | MIN |  |  | PAC | 2014-08-14 | REDMOND
REDMOND | 115 |  | 116 |  | 116 | 116 |  | +2.0/-1.0 |  | PAC, PGE | 1984-01-01 | REDMOND
REDMOND | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1991-02-01 | REDMOND
REEDSPORT | 115 |  | 118 |  | 117 | 116 |  | +2.0/-2.0 |  |  | 1992-02-01 | REEDPORT
RICHLAND | 115 |  | 119 |  | 118 | 117 |  | +2.0/-2.0 |  |  | 1987-02-01 | RICHLAND
ROCK CREEK | 230 | 239.5 | 242 | MAX |  | 237 | MIN |  |  |  | 2013-12-13 | ROCKCREK
ROGUE | 115 |  | 119 |  | 118 | 117 |  | +2.0/-2.0 |  |  | 1992-02-01 | ROGUE
ROGUE | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  | CCPUD | 1985-01-01 | ROGUE
ROSS | 69 |  | 70 |  | 69 | 68 |  | +1.5/-3.0 |  | CCPUD | 1979-07-01 | ROSS
ROSS | 115 |  | 119 |  | 118 | 117 |  | +2.0/-4.0 |  |  | 1966-03-01 | ROSS
ROSS | 230 |  | 239 |  | 236 | 234 |  | +3.0/-3.0 |  | PAC | 1982-02-01 | ROSS
ROUNDUP | 69 | 70.75 | 72.5 | MAX |  | 69 | MIN |  |  | PAC | 1991-02-01 | ROUNDUP
ROUNDUP | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1985-01-01 | ROUNDUP
ROUND VALLEY | 69 | 71 | 73 | MAX |  | 69 | MIN |  |  |  | 1988-02-01 | ROUND_VL
SACAJAWEA | 115 |  | 120 |  | 119 | 118 |  | +1.0/-4.0 | SUMMER (MAY-SEPT) |  | 1988-02-01 | SACAJWEA
SACAJAWEA | 115 |  | 119 |  | 118 | 117 |  | +1.0/-4.0 | WINTER (OCT-APRIL) |  | 1988-02-01 | SACAJWEA
SACAJAWEA | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  |  | 1987-02-01 | SACAJWEA
SACHEEN | 115 |  | 117 |  | 116 | 115 |  | +2.0/-2.0 |  |  | 1992-02-01 | SACHEEN
SACHEEN | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  | PAC, PGE | 2000-03-01 | SACHEEN
SALEM | 115 |  | 119 |  | 118 | 117 |  | +2.0/-3.0 |  | PAC | 1992-02-01 | SALEM
SALEM | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  | Avista | 1980-01-01 | SALEM
SAND CREEK | 115 |  | 117 |  | 117 | 117 |  | +2.0/-2.0 |  | PAC | 2000-03-01 | SAND_CRK
SANTIAM | 69 |  | 69.5 |  | 69 | 68.5 |  | +2.0/-1.5 |  | PAC | 1975-01-01 | SANTIAM
SANTIAM | 230 |  | 239 |  | 236 | 234 |  | +3.0/-4.0 |  |  | 1992-02-01 | SANTIAM
SATSOP | 230 | 238.5 | 242 | MAX |  | 235 | MIN |  |  |  | 2013-12-13 | SATSOP
SATSOP | 500 | 535 | 550 | MAX |  | 520 | MIN |  |  |  | 1985-01-01 | SATSOP
SCHULTZ | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  |  | 2000-03-01 | SCHULTZ
SHELTON | 115 |  | 118 |  | 118 | 118 |  | +2.0/-2.0 | Var coordination at Kitsap/Oly | PSE | 2003-03-03 | SHELTON
SHELTON | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  | DCPUD | 1980-01-01 | SHELTON
SICKLER | 230 |  | 238 |  | 238 | 238 |  | +2.0/-2.0 |  |  | 2007-05-07 | SICKLER
SICKLER | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  | CCPUD | 1994-02-01 | SICKLER
SIFTON | 115 |  | 119 |  | 118 | 117 |  | +2.0/-6.0 |  |  | 1980-01-01 | SIFTON
SIFTON | 230 |  | 239 |  | 236 | 234 |  | +3.0/-6.0 |  |  | 1982-02-01 | SIFTON
SILVER CREEK | 69 | 70.75 | 72.5 | MAX |  | 69 | MIN |  |  | PGE | 1991-02-01 | SILVER CREEK
SLATT | 500 | 542 | 550 | MAX |  | 535 | MIN |  |  |  | 2018-07-01 | SLATT
SLATT | 230 | 239 | 242 | MAX |  | 236 | MIN |  |  | PSE, SCPUD | 2011-09-11 | SLATT
SNOHOMISH | 115 |  | 115 |  | 114 | 113 |  | +2.0/-2.0 |  | PSE, SCL | 1985-12-01 | SNOHOMSH
SNOHOMISH | 230 |  | 238 |  | 236 | 234 |  | +3.0/-1.0 |  | PSE, SCPUD | 1988-05-01 | SNOHOMSH
SNOKING | 115 |  | 115 |  | 114 | 113 |  | +3.0/-1.0 | request of the PUD | PSE, SCL | 2003-08-01 | SNO_KING
SNOKING | 230 | 238 | 240 | MAX |  | 235 | MIN |  |  |  | 2005-12-05 | SNO_KING
South Bremerton(PSE) | 115 | 118 | 121 | MAX |  | 115 | MIN |  |  |  | 2002-01-01 | S_BREMER
South Tacoma | 230 | 238.5 | 242 | MAX |  | 235 | MIN |  | Frederickson LLP |  | 2011-09-11 | S_TACOMA
SPAR CANYON | 230 | 240 | 242 | MAX |  | 230 | MIN |  |  |  | 1995-03-01 | SPAR_CYN
ST. JOHNS | 57 | 59.5 | 60.5 | MAX |  | 58.5 | MIN |  |  | PGE | 1990-02-01 | ST_JOHNS
ST. JOHNS | 115 |  | 117 |  | 116 | 115 |  | +3.0/-3.0 |  | PAC | 1990-02-01 | ST_JOHNS
SUMMER LAKE (PP&L) | 500 | 542.5 | 550 | MAX |  | 535 | MIN |  |  |  | 2004-12-04 | SUMMERLK
SWAN VALLEY | 115 | 119 | 121 | MAX |  | 115 | MIN |  |  | TPWR | 1995-03-01 | SWAN_VLY
TACOMA | 230 | 238 | 240 | MAX |  | 235 | MIN |  |  |  | 2005-12-05 | TACOMA
TACOMA | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  |  | 1988-02-01 | TACOMA
TAFT | 500 | 542.5 | 550 | MAX |  | 535 | MIN |  |  |  | 2004-12-04 | TAFT
TAHKENITCH | 115 |  | 119 |  | 118 | 116 |  | +2.0/-2.0 |  |  | 1992-02-01 | TAHKNICH
TAHKENITCH | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1980-01-01 | TAHKNICH
TARGHEE | 46 | 48 | 48.3 | MAX |  | 46 | MIN |  |  |  | 1995-03-01 | TARGHEE
TARGHEE | 115 | 119 | 121 | MAX |  | 115 | MIN |  |  |  | 1995-03-01 | TARGHEE
TETON | 115 | 119 | 121 | MAX |  | 115 | MIN |  |  |  | 1995-03-01 | TETON
THE DALLES | 115 |  | 120 |  | 119 | 118 |  | +5.0/-6.0 |  |  | 1991-02-01 | T_DALLES
TILLAMOOK | 115 |  | 118 |  | 117 | 116 |  | +2.0/-2.0 |  |  | 1992-02-01 | TILLAMOK
TIN CUP | 115 | 119 | 122 | MAX |  | 115 | MIN |  |  |  | 2017-12-17 | TINCUP
TOLEDO | 69 |  | 70 |  | 69 | 68 |  | +1.0/-2.0 |  |  | 1980-01-01 | TOLEDO
TOLEDO | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  | Avista | 1980-01-01 | TOLEDO
TRENTWOOD | 115 | 117.5 | 120 | MAX |  | 115 | MIN |  |  | PAC, PGE | 1991-02-01 | TRENTWOD
TROUTDALE | 230 |  | 240 |  | 238 | 236 |  | +3.0/-4.0 |  |  | 1992-02-01 | TROUTDAL
TUCANNON RIVER | 115 | 120 | 122 | MAX |  | 118 | MIN |  |  |  | 2015-04-01 | TUCANRVR
USK | 230 | 235 | 240 | MAX |  | 230 | MIN |  |  | CHPUD, DCPUD | 1989-01-01 | USK
VALHALLA | 115 | 118 | 121 | MAX |  | 115 | MIN |  |  | GCPUD | 1991-02-01 | VALHALLA
VANTAGE | 230 |  | 239 |  | 239 | 239 |  | +4.0/-2.0 | 239 kV FLAT SCHEDULE to coordinate with |  | 2015-04-15 | VANTAGE
Grant PUD Wanapum voltage schedule
VANTAGE | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  | PAC | 1988-02-01 | VANTAGE
WALLA WALLA | 69 | 69.75 | 71.5 | MAX |  | 68 | MIN |  |  | PAC | 1992-02-01 | WALAWALA
WALLA WALLA | 115 | 117.5 | 121 | MAX |  | 114 | MIN |  |  |  | 1995-02-01 | WALAWALA
WARNER | 115 |  | 120 |  | 120 | 120 |  | +4.0/-2.0 |  |  | 1987-01-01 | WARNER
WARNER | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1987-01-01 | WARNER
WAUTOMA | 500 | 540 | 550 | MAX |  | 530 | MIN |  |  |  | 2007-12-07 | WAUTOMA
WENDSON | 115 |  | 119 |  | 118 | 117 |  | +2.0/-3.0 |  |  | 1992-02-01 | WENDSON
WENDSON | 230 | 236 | 242 | MAX |  | 230 | MIN |  |  |  | 1980-01-01 | WENDSON
WHITE BLUFFS | 115 |  | 120 |  | 119 | 118 |  | +2.0/-3.0 | SUMMER (MAY-SEPT) |  | 1987-02-01 | WHITE_BL
WHITE BLUFFS | 115 |  | 119 |  | 118 | 117 |  | +2.0/-3.0 | WINTER (OCT-APRIL) |  | 1988-02-01 | WHITE_BL

## SUB SCHEDULES (SEASONAL)
SUBSTATION SCHEDULES
STATION | BUS KV | TARGET (kV) | HI | MED | LOW | BAND (+/- kV) | REMARKS | TOP Interface | DATE
BADGER CANYON | 115 |  | 120 | 119 | 118 | +2.0/-2.0 | SUMMER (MAY-SEPT) |  | 1987-02-01
BADGER CANYON | 115 |  | 119 | 118 | 117 | +2.0/-2.0 | WINTER (OCT-APRIL) |  | 1988-02-01
BENTON | 115 |  | 119 | 119 | 119 | +2.0/-2.0 | SUMMER (MAY-SEPT) |  | 2017-12-17
BENTON | 115 |  | 118 | 118 | 118 | +2.0/-1.0 | WINTER (OCT-APRIL) |  | 2017-12-17
FRANKLIN | 115 |  | 120 | 119 | 118 | +2.0/-2.0 | SUMMER (MAY-SEPT) |  | 1988-02-01
FRANKLIN | 115 |  | 119 | 118 | 117 | +2.0/-2.0 | WINTER (OCT-APR) |  | 1988-02-01
HORSE HEAVEN | 115 |  | 119 | 119 | 119 | +2.0/-2.0 | SUMMER (MAY-SEPT) request by BCPUD |  | 2017-12-17
HORSE HEAVEN | 115 |  | 118 | 118 | 118 | +2.0/-2.0 | WINTER (OCT-APRIL) request by BCPUD |  | 2017-12-17
MCNARY | 115 |  | 120 | 119 | 118 | +3.0/-3.0 | SUMMER (MAY-SEPT) | PAC | 1979-01-01
MCNARY | 115 |  | 119 | 118 | 117 | +3.0/-3.0 | WINTER (OCT-APRIL) |  | 1988-02-01
MCNARY | 230 |  | 242 | 240 | 238 | +3.0/-4.0 | SUMMER (MAY-SEP) | PGE | 1993-03-01
MCNARY | 230 |  | 240 | 239 | 238 | +3.0/-4.0 | WINTER (OCT-APRIL) |  | 2009-04-09
MIDWAY | 115 |  | 120 | 119 | 118 | +3.0/-4.0 | SUMMER (MAY-SEPT) | PAC | 1981-01-01
MIDWAY | 115 |  | 119 | 118 | 117 | +3.0/-4.0 | WINTER (OCT-APRIL) |  | 1988-02-01
SACAJAWEA | 115 |  | 120 | 119 | 118 | +1.0/-4.0 | SUMMER (MAY-SEPT) |  | 1988-02-01
SACAJAWEA | 115 |  | 119 | 118 | 117 | +1.0/-4.0 | WINTER (OCT-APRIL) |  | 1988-02-01
WHITE BLUFFS | 115 |  | 120 | 119 | 118 | +2.0/-3.0 | SUMMER (MAY-SEPT) |  | 1987-02-01
WHITE BLUFFS | 115 |  | 119 | 118 | 117 | +2.0/-3.0 | WINTER (OCT-APRIL) |  | 1988-02-01

## GEN SCHEDULES
GENERATION SCHEDULES
PLANT | BUS KV | TARGET | HI |  | MED | LOW |  | BAND (+/- kV) | REFERENCE VOLTAGE | DATE | REMARKS | NOTES | TOP Interface | SCADA ID | WECC Case Regulated Bus | WECC Case Gen Bus
FEDERAL-----------------------------
ALBENI FALLS | 115 | 117 | 117 |  | 117 | 117 |  | 3 | Albeni Falls 115 bus | 1992-02-01 | Flat 117kV schedule |  | Avista | ALBENI_F | 40029 | 40028 | 40030 | 40032
BONNEVILLE | 115 |  | 120 |  | 119 | 118 |  | 2.5 | Bonneville PH 115 bus | 2009-12-09 |  |  | CCPUD | BONNVILL | 40139 | 44001 | 44005
DWORSHAK | 115 | 115 | 115 |  | 115 | 115 |  | 3 | Dworshak 115 bus | 1978-05-01 |  |  |  | DWORSHAK | 40367 | 40361
FOSTER | 115 | 118 | 121 | MAX |  | 115 | MIN | 3 | Foster 115 bus | 2010-08-01 |  |  |  | FOSTER | 40435 | 44032 | 44031
GRAND COULEE(USBR) | 115 |  | 120 |  | 117 | 116 |  | 3 | Grand Coulee 115 bus | 2016-03-01 |  |  | DCPUD | GRAND COULEE(USBR)
ICE HARBOR | 115 |  | 119 |  | 118 | 117 |  | 3 | Ice Harbor 115 bus | 1988-02-01 | WINTER (OCT-APRIL) |  |  | ICE HARBOR | 40565 | 40559 | 40560
[15 empty] | 40567 | 40561 | 40562
ICE HARBOR | 115 |  | 120 |  | 119 | 118 |  | 3 | Ice Harbor 115 bus | 1982-02-01 | SUMMER (MAY-SEP) |  |  | ICE HARBOR | 40569 | 40563 | 40564
LOOKOUT PT. | 115 | 118 | 121 | MAX |  | 115 | MIN | 3 | Lookout Pt 115 bus | 2010-08-01 |  |  |  | LOOKOUT PT. | 41229 | 44273 | 44272 | 44271
MCNARY | 115 |  | 120 |  | 119 | 118 |  | 3 | McNary 115 bus | 1979-01-01 | SUMMER (MAY-SEP) |  |  | MCNARY | 40718 | 44113 | 44114
MCNARY | 115 |  | 119 |  | 118 | 117 |  | 3 | McNary 115 bus | 1988-02-01 | WINTER (OCT-APRIL) |  |  | MCNARY
MINIDOKA(USBR) | 138 | 143.5 | 145 | MAX |  | 139 | MIN | 3.5 | Minidoka 138 bus | 2020-11-10 |  |  |  | MINIDOKA(USBR) | 61810 | 61812 | 61811
PALISADES(USBR) | 115 | 118.5 | 121 | MAX |  | 116 | MIN | 2.5 | Palisades 115 bus | 2005-01-05 |  |  |  | PALISADE | 66185 | 66175 | 66170 | 66165 | 66160
THE DALLES | 115 |  | 120 |  | 119 | 118 |  | 3 | Big Eddy 115 bus | 1992-03-01 |  |  |  | THE DALLES | 40107 | 44041 | 44042
BONNEVILLE | 230 |  | 239 |  | 236 | 234 |  | 2 | North Bonneville 230 bus | 1978-08-01 |  |  |  | BONNEVILLE | 40141 | 44002 | 44003 | 44004 | 44006 | 44007 | 44008 | 44009
CHIEF JOSEPH | 230 |  | 240 |  | 238 | 236 |  | 2 | Chief Jo 230 bus | 2000-03-01 |  |  |  | CHIEF JOSEPH | 40230 | 44141 | 44142 | 44143 | 44144 | 44145 | 44146 | 44147 | 44148
DETROIT, BIG CLIFF | 230 | 236.5 | 239 | MAX |  | 234 | MIN | 4 | Detroit 230 bus | 2010-08-01 |  |  |  | DETROIT, BIG CLIFF | 40230: 40345; 44141: 41303; 44142: 403441; 44143: 403442
GRAND COULEE(USBR) | 230 |  | 240 |  | 238 | 236 |  | 3 | Grand Coulee 230 bus | 1993-03-01 |  |  |  | G_COULEE | 41357 | 41721 | 41722 | 41723 | 41724 | 41725 | 40282 | 40284 | 40286
[15 empty] | 41357 | 41726 | 41727 | 41728 | 41729 | 41730 | 41731 | 41732 | 41733
[15 empty] | 41357 | 41738 | 41737 | 41736 | 41735 | 41734
HUNGRY HORSE(USBR) | 230 |  | 239 |  | 237 | 235 |  | 2 | Hungry Horse 230 bus | 1972-10-01 | MOUNTAIN-STD-TIME |  |  | HUNGRY HORSE(USBR) | 41357: 40557; 41726: 40555; 41727: 40556
LIBBY | 230 |  | 240 |  | 237 | 235 |  | 2 | Libby 230 bus | 1975-07-01 | MST |  |  | LIBBY | 40657 | 44191 | 44192 | 44193 | 44194 | 44195
MCNARY | 230 |  | 242 |  | 240 | 238 |  | 3 | McNary 230 bus | 1993-03-01 | SUMMER (MAY-SEP) | Seasonal change made on SCADA/Overviews\ |  | MCNARY | 41357: 41352; 41726: 44101; 41727: 44102; 41728: 44103; 41729: 44104
[12 empty] | VARRES Plant Info\Plant Summary. Select McNary |  |  | 41357: 41352; 41726: 44105; 41727: 44106; 41728: 44107; 41729: 44108
MCNARY | 230 |  | 240 |  | 239 | 238 |  | 3 | McNary 230 bus | 2009-04-09 | WINTER (OCT-APRIL) | then Shift left click Change Sched. |  | MCNARY | 41357: 41352; 41726: 44109; 41727: 44110; 41728: 44111; 41729: 44112
THE DALLES | 230 |  | 240 |  | 239 | 236 |  | 2 | Big Eddy 230 bus | 1999-02-01 |  |  |  | THE DALLES | 41357: 41342; 41726: 44043; 41727: 44044
[15 empty] | 41342 | 44045 | 44046
[15 empty] | 41342 | 44047 | 44048
[15 empty] | 41342 | 44049 | 44050 | 44051
CHIEF JOSEPH | 500 | 539 | 539 |  | 539 | 539 |  | 2 | Chief Jo 500 bus | 2016-03-01 |  |  |  | CHIEF JOSEPH | 40233 | 44151 | 44152 | 44153 | 44150 | 44149 | 44154
DWORSHAK | 500 | 540 | 540 |  | 540 | 540 |  | 4 | Dworshak 500 bus | 1984-03-01 |  |  |  | DWORSHAK | 41357: 40369; 41726: 40365; 41727: 40363
GRAND COULEE(USBR) | 500 | 542 | 542 |  | 542 | 542 |  | 2 | Grand Coulee 500 bus | 2016-03-01 |  |  |  | G_COULEE | 40287 | 40291 | 40293 | 40295 | 40296 | 40297 | 40298
JOHN DAY | 500 |  | 542 |  | 540 | 540 |  | 2 | John Day 500 bus | 2008-09-08 |  |  |  | JOHN DAY | 40585 | 44071 | 44072 | 44073 | 44074 | 44075 | 44076 | 44077 | 44078
LITTLE GOOSE | 500 | 540 | 540 |  | 540 | 540 |  | 2.5 | Little Goose 500 bus | 1982-12-01 |  |  |  | LITTLE GOOSE | 41357: 40665; 41726: 44211; 41727: 44212; 41728: 44213; 41729: 44214
LOWER GRANITE | 500 | 540 | 540 |  | 540 | 540 |  | 3 | Lower Granite 500 bus | 1982-12-01 |  |  |  | LOWER GRANITE | 41357: 40679; 41726: 44231; 41727: 44232; 41728: 44233; 41729: 44234
LOWER MONUMENTAL | 500 | 540 | 540 |  | 540 | 540 |  | 2 | Lower Monumental 500 bus | 1982-12-01 |  |  |  | LOW_MON | 41357: 40683; 41726: 44251; 41727: 44252; 41728: 44253; 41729: 44254
Additional Willamette Valley Plants | [13 empty] | Additional Willamette Valley Plants
COUGAR | 6.9 | 6.9 | 7.1 | MAX |  | 6.7 | MIN | 0.4 | Generator terminal | 2010-08-01 |  |  |  | COUGAR | 41357: 41304; 41726: 41304
DEXTER | 13.8 | 13.8 | 14.2 | MAX |  | 13.4 | MIN | 0.8 | Generator terminal | 2010-08-01 |  |  |  | DEXTER | 41357: 40346; 41726: 40346
GREEN PETER | 13.8 | 13.8 | 14.2 | MAX |  | 13.4 | MIN | 0.8 | Generator terminal | 2010-08-01 |  |  | PAC | GREEN PETER | 41357: 40484; 41726: 40484
HILLS CREEK | 6.9 | 6.9 | 7.1 | MAX |  | 6.7 | MIN | 0.4 | Generator terminal | 2010-08-01 |  |  |  | HILLS CREEK | 41357: 41213; 41726: 41213
NON-FEDERAL--------------------- | [13 empty] | NON-FEDERAL---------------------
BOX CANYON (PEND OREILLE) | 115 | 117 | 117 |  | 117 | 117 |  | 3 | POI | 2018-07-01 | PEND OREILLE PUD(AVISTA) |  |  | BOX CANYON (PEND OREILLE) | 41357: 47009; 41726: 47010; 41727: 47012; 41728: 47014; 41729: 47016
CARMEN SMITH (EWEB) | 115 |  | 123 | MAX |  | 116 | MIN | 2 | POI | 2020-11-20 | May exceed 122kV due to radial config. and generation configuration | Per EWEB, Carmen Smith station’s installed equipment is rated to 138kV |  | CARMEN SMITH (EWEB) | 41357: 46211; 41726: 46210
HOPKINS RIDGE (PSE) | 115 | 119 | 121 | MAX |  | 116 | MIN | 2.5 | POI | 2020-11-20 |  |  | PSE request for 119-kV target | HOPKINS RIDGE (PSE) | 41357: 41400; 41726: 47878
[15 empty] | 41400 | 47879
HORN BUTTE (Willlow Creek Energy LLC) | 115 | 118 | 121 | MAX |  | 115 | MIN | 3 | POI | 2020-11-20 | see Boardman 115 |  |  | HORN_BTE | 41357: 41404; 41726: 47995
HORSE BUTTE | 115 | 118 | 121 | MAX |  | 115 | MIN | 3 | POI | 2012-06-12 | in PACE BAA |  |  | HORSE BUTTE | 41357: 66546; 41726: 66550
LONGVIEW FIBER | 115 | 117.5 | 120 | MAX |  | 115 | MIN | 2.5 | POI |  |  |  |  | LONGVIEW FIBER | 41357: 40309; 41726: 47447; 41727: 47448; 41728: 47446
McKinley Paper Biomass | 69 | 69 | 71 | MAX |  | 67 | MIN | 2 | POI | 2013-09-03 | see Port Angeles 69 | previously Nippon Paper |  | McKinley Paper Biomass | 41357: 40841; 41726: 408412
NINE CANYON (BENTON) | 115 | 119 | 121 | MAX |  | 117 | MIN | 2 | POI | 2008-12-08 | see Badger Canyon 115 |  |  | NINE CANYON (BENTON) | 41357: 41388; 41726: 47956; 41727: 47948; 41728: 47952
NINEMILE (Next Era Energy) | 115 | 118 | 120 | MAX |  | 116 | MIN | 2 | POI |  |  |  |  | NINEMILE (Next Era Energy) | 41357: 47574; 41726: 47964
PACKWOOD (Energy Northwest) | 69 | 70 | 72 | MAX |  | 68 | MIN | 2 | POI | 2013-12-13 |  |  |  | PACKWOOD (Energy Northwest) | 41357: 47047; 41726: 470473
RIVER ROAD (CPUD) | 115 | 118 | 121 | MAX |  | 115 | MIN | 3 | POI | 2018-12-18 |  |  |  | RIVER ROAD (CPUD) | 41357: 47215; 41726: 47216
WEYCO 3 (International Paper, EWEB) | 115 |  | 120 |  | 119 | 118 |  | 3 | Weyco 3 | 2020-01-20 |  |  |  | WEYCO 3 (International Paper, EWEB) | 41357: 46267; 41726: 46268
ARLINGTON WIND, RATTLESNAKE ROAD (EDP) | 230 | 241 | 242 | MAX |  | 237 | MIN | 3.5 | POI | 2020-11-20 |  |  |  | ARLINGTON WIND, RATTLESNAKE ROAD (EDP) | 41357: 47814; 41726: 47892
BIG HORN 1 & 2 (Avangrid) | 230 | 238.5 | 242 | MAX |  | 235 | MIN | 3.5 | POI | 2008-12-08 |  |  |  | BIG_HORN | 41357: 40686; 41726: 47872
[15 empty] | 40686 | 47799 | 47873
BIGLOW CANYON (PGE) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2009-09-09 | see John Day 230 |  | PGE | BIGLOW CANYON (PGE) | 41357: 47844; 41726: 47933; 41727: 47983; 41728: 47985
BOUNDARY PH (SCL) | 230 | 240 | 240 |  | 240 | 240 |  | 2 | POI | 2018-07-01 | SCL |  |  | BOUNDARY PH (SCL) | 40145 | 46464 | 46466 | 46470 | 46472 | 46468 | 46474
COWLITZ FALLS (Lewis PUD) | 230 | 238.5 | 242 | MAX |  | 235 | MIN | 3.5 | Glenoma 230kV station | 2008-08-08 |  |  |  | COWLITZ FALLS (Lewis PUD) | 41357: 47049; 41726: 40307
DODGE JUNCTION | 230 | 238 | 242 | MAX |  | 234 | MIN | 4 | POI | 2014-02-01 |  |  |  | DODGE JUNCTION | 41357: 42987; 41726: 42994
DOOLEY (Klickitat PUD, Windy Point Partners LLC) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2010-08-10 | see Rock Creek 230 |  |  | DOOLEY (Klickitat PUD, Windy Point Partners LLC) | 41357: 41402; 41726: 47498; 41727: 47495
EE CLOUSE (Goldendale) | 230 | 239 | 242 | MAX |  | 236 | MIN | 3 | POI | 2012-01-12 | see Harvalum |  |  | EE CLOUSE (Goldendale) | 41357: 47329; 41726: 47688; 41727: 47687
ENERGIZER (Klickitat PUD, Windy Point Wind LLC) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2009-09-09 | see Rock Creek 230 |  |  | ENERGIZE | 41357: 41402; 41726: 47937
FREDERICKSON LLP | 230 | 238.5 | 242 | MAX |  | 235 | MIN | 3.5 | POI | 2011-09-11 | see S. Tacoma |  |  | FREDERICKSON LLP | 41357: 41055; 41726: 47577; 41727: 47576
GOLDEN HILLS (Avangrid) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2021-12-21 | see John Day 230 |  |  |  | 41357: 47844; 41726: 47489
GRAYS HARBOR ENERGY (LLC) | 230 | 238.5 | 242 | MAX |  | 235 | MIN | 3.5 | POI | 2009-09-09 | see Satsop |  |  | GRAYS_H | 41357: 40947; 41726: 47596; 41727: 47597; 41728: 47598
HARVEST WIND (Klickitat PUD) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2010-08-10 | see Rock Creek 230 |  |  | HARVEST WIND (Klickitat PUD) | 41357: 41402; 41726: 47981
HAY CANYON (Iberdrola) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2009-09-09 | see John Day 230 |  |  | HAY CANYON (Iberdrola) | 41357: 47830; 41726: 47974
HERMISTON (Hermiston Generating Plant) | 230 |  | 242 |  | 240 | 238 |  | 3 | McNary 230 bus | 2009-04-08 | SUMMER (MAY-SEP) | Seasonal change made on SCADA/Overviews\ |  | HERMISTON (Hermiston Generating Plant) | 41357: 41352; 41726: 45454; 41727: 45455; 41728: 45456; 41729: 45457
VARRES Plant Info\Plant Summary. Select Hermiston
HERMISTON (Hermiston Generating Plant) | 230 |  | 240 |  | 239 | 238 |  | 3 | McNary 230 bus | 2009-04-09 | WINTER (OCT-APRIL) | then Shift left click Change Sched. | PAC | HERMISTON (Hermiston Generating Plant)
IMRIE (Goodnoe Hills) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2013-12-13 | see Rock Creek 230 |  |  | IMRIE (Goodnoe Hills) | 41357: 41402; 41726: 47866
JUNIPER CANYON | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2013-12-13 | see Rock Creek 230 |  |  | JUNIPER CANYON | 41357: 41402; 41726: 47389
KITTITAS VALLEY | 230 | 239 | 242 | MAX |  | 236 | MIN | 3 | POI | 2013-12-13 |  |  |  | KITTITAS VALLEY | 41357: 44276; 41726: 44279
[15 empty] | 44277 | 44277 | SVC
KLONDIKE SCHOOLHOUSE I & II & III & IIIa (Avangrid) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2009-09-09 | see John Day 230 |  |  | KLNDSCHL | 41357: 47830; 41726: 47921
[15 empty] | 47830 | 47924
[15 empty] | 47830 | 47926 | 47925
[15 empty] | 47830 | 47912
[15 empty] | 47830 | 47917
LUND HILL (Avangrid) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2021-12-21 | see Rock Creek 230 |  |  |  | 41357: 41402; 41726: 473851
LEANING JUNIPER I (PACW) | 230 | 241 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2020-11-20 |  |  |  | LEANING JUNIPER I (PACW) | 41357: 47814; 41726: 44885
LEANING JUNIPER IIA & IIB (Avangrid) | 230 | 241 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2020-11-20 |  |  |  | LEANJUN2 | 41357: 47814; 41726: 47806
[15 empty] | 47814 | 47810
LINDEN WIND | 230 | 239 | 242 | MAX |  | 236 | MIN | 3 | POI | 2012-01-12 | see Harvalum |  |  | LINDEN_C | 41357: 47381; 41726: 47384
MINT FARM | 230 | 237.5 | 240 | MAX |  | 234 | MIN | 3 | Mint Farm 230 bus | 2013-12-13 | Puget Sound Energy |  |  | MINT FARM | 41357: 47677; 41726: 47675; 41727: 47676
MONTAGUE 1 & 2 (Avangrid) | 230 | 239 | 242 | MAX |  | 236 | MIN | 3 | POI | 2021-12-21 | See Slatt 230 |  |  |  | 41357: 47849; 41726: 47378; 41727: 47397
PEBBLE SPRINGS (Avangrid) | 230 | 241 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2020-11-20 |  |  |  | PEBBLE SPRINGS (Iberdrola) | 41357: 47814; 41726: 47887
PRIEST RAPIDS (GRANT) | 230 | 240 | 240 |  | 240 | 240 |  | 2 | Priest Rapids 230 bus | 2016-03-01 | GRANT COUNTY PUD - maintain |  | GCPUD | PRIEST RAPIDS (GRANT) | 41357: 41347; 41726: 46170; 41727: 46171; 41728: 46172; 41729: 46173
[11 empty] | flat 240kV per Grant PUD voltage schedule |  |  |  | 41357: 41347; 41726: 46178; 41727: 46179
[15 empty] | 41347 | 46174 | 46175 | 46176 | 46177
PHALEN GULCH | 230 | 238 | 242 | MAX |  | 234 | MIN | 4 | POI | 2014-02-01 |  |  |  | PHALEN GULCH | 41357: 42987; 41726: 42990
RATHDRUM POWER (LANCASTER) | 230 | 240 | 242 | MAX |  | 238 | MIN | 2 | Lancaster 230 bus | 2013-12-13 |  |  |  | RATHDRUM POWER (LANCASTER) | 41357: 40624; 41726: 47569; 41727: 47568
ROCKY REACH (CHELAN) | 230 | 238 | 238 |  | 238 | 238 |  | 2 | POI | 2007-05-07 | CHELAN COUNTY PUD - maintain |  | CHPUD | ROCKY_RH | 41357: 46832; 41726: 46841; 41727: 46842; 41728: 46843; 41729: 46844
[11 empty] | flat 238kV in coordination w/ BPA |  |  |  | 46832 | 46845 | 46846 | 46847 | 46848 | 46849
[15 empty] | 46832 | 46850 | 46851
SHEPHERDS CENTRAL (S. HURLBURT WIND) | 230 | 239 | 242 | MAX |  | 236 | MIN | 3 | POI |  | See Slatt 230 |  |  | SOUTH HURLBURT WIND (GE Remote) | 41357: 47849; 41726: 47464; 41727: 47469
SHEPHERDS NORTH (N. HURLBURT WIND) | 230 | 239 | 242 | MAX |  | 236 | MIN | 3 | POI |  | See Slatt 230 |  |  | NORTH HURLBURT WIND (GE Remote) | 41357: 47849; 41726: 47452; 41727: 47455
SHEPHERDS SOUTH (HORSESHOE BEND) | 230 | 239 | 242 | MAX |  | 236 | MIN | 3 | POI |  | See Slatt 230 |  |  | HORSESHOE BEND | 41357: 47849; 41726: 47458
[15 empty] | 47849 | 47461
STAR POINT (Avangrid) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2013-12-13 | see John Day 230 |  |  | STAR POINT (Iberdrola) | 41357: 47971; 41726: 47975
TUCANNON RIVER (Mullan, PGE) | 230 | 238 | 242 | MAX |  | 234 | MIN | 4 | POI | 2014-12-14 |  |  | PGE | TUCANNON RIVER (Mullan, PGE) | 41357: 43950; 41726: 43953
[15 empty] | 43950 | 43956
WANAPUM (GRANT) | 230 |  | 239 |  | 239 | 239 |  | 3 | Wanapum 230 bus | 2015-04-15 | Agreement with |  | GCPUD | WANAPUM (GRANT) | 46169 | 46180 | 46181 | 46182 | 46183 | 46184 | 46185 | 46186 | 46187 | 46188 | 46189
GCPUD
WHEATFIELD (Horizon) | 230 | 241 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2020-11-20 |  |  |  | WHEATFIELD (Horizon) | 46169: 47814; 46180: 47897
WHEATRIDGE 1 & 2 (Blue Ridge) | 230 | 240 | 242 | MAX |  | 235 | MIN | 2 | POI | 2020-07-20 |  |  |  | BLUE RIDGE (Wheatridge Wind) | 46169: 47600; 46180: 47603; 46181: 47602; 46182: 47601
[15 empty] | 47600 | 47607 | 47606 | Blue Ridge Solar Placeholder
WELLS (DOUGLAS) | 230 |  | 241 |  | 238 | 236 |  | 3 | Douglas 230 bus | 2007-05-07 | DOUGLAS CO PUD |  |  | WELLS (DOUGLAS) | 46169: 47031; 46180: 47104; 46181: 47105; 46182: 47106; 46183: 47107; 46184: 47108
WHITE CREEK (WC Wind I LLC) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2009-09-09 | see Rock Creek 230 |  |  | WHITE CREEK (WC Wind I LLC) | 46169: 41402; 46180: 47906
[15 empty] | 41402 | 47907
WILLIS (Klickitat PUD, Tuolumne Wind LLC) | 230 | 239.5 | 242 | MAX |  | 237 | MIN | 2.5 | POI | 2009-09-09 | see Rock Creek 230 |  |  | WILLIS | 46169: 41402; 46180: 47939; 46181: 47940
ASHE CGS | 500 | 540 | 540 |  | 540 | 540 |  | 3 | Ashe 500 bus | 1984-03-01 | Energy Northwest |  |  | ASHE CGS | 46169: 40061; 46180: 40063
CALPINE (HPP) | 500 | 542 | 545 | MAX |  | 538 | MIN | 3.5 | McNary 500 bus | 2013-12-13 |  |  |  | CALPINE (HPP) | 46169: 40723; 46180: 47639; 46181: 47640; 46182: 47641
CARTY (PGE) | 500 | 544 | 550 | MAX |  | 538 | MIN | 3.5 | Slatt 500 bus | 2016-03-01 |  |  | PGE | CARTY (PGE) | 46169: 40989; 46180: 43044; 46181: 43045
CENTRALIA (Trans-Alta) | 500 | 540 | 540 |  | 540 | 540 |  | 2.5 | Paul 500 bus | 2005-01-04 |  |  |  | CENTRALIA (Trans-Alta) | 46169: 40821; 46180: 47740; 46181: 47744
CHEHALIS POWER | 500 | 540 | 545 | MAX |  | 535 | MIN | 3 | Napavine 500 bus | 2009-09-09 | see Napavine |  |  | CHEHALIS POWER | 46169: 40774; 46180: 47588; 46181: 47589; 46182: 47590
COYOTE SPRINGS #1 and #2 | 500 | 542 | 550 | MAX |  | 538 | MIN | 3.5 | Coyote Springs 500 bus | 2018-07-01 |  |  |  | COYOTE SPRINGS #1 and #2 | 46169: 43123; 46180: 43111; 46181: 48516; 46182: 43119; 46183: 48518

## Revision History
REVISION HISTORY
DESCRIPTION | DATE | INITIALS
Voltage Schedule Cover date changed from 2021 to 2022 | 2022-01-19 | JW
Added Bonners Ferry and Ellensburg to sub schedules Added Montague 1 & 2 (Avangrid) to Gen Schedules Added Shepherds Flat naming to Horseshoe Bend, N and S Hurlburt wind sites Added Lundhill (Avangrid) to Gen Schedules Added Golden Hills (Avangrid) to Gen Schedules Changed BLUERIDGE (Wheatridge wind) to WHEATRIDGE 1 & 2 (Blue Ridge) Added Raver 230 sub schedule Changed BIG HORN (Iberdrola) to BIG HORN 1 &2 (Avangrid) Changed KLONDIKE SCHOOLHOUSE II & III (Iberdrola) to KLONDIKE SCHOOLHOUSE I & II & III & IIIa (Avangrid) Changed LEANING JUNIPER II (Iberdrola) to LEANING JUNIPER IIA & IIB (Avangrid) Changed PEBBLE SPRINGS (Iberdrola) to PEBBLE SPRINGS (Avangrid) Changed STAR POINT (Iberdrola) to STAR POINT (Avangrid) Added Morrow Flat 230 &115kV sub schedule Added Quenett Creek 230 sub schedule | 2021-12-17 | JW
End of year update and holiday update. Carmen Smith high limit changed to 123kV from 121kV and band adjusted to 2kV with EWEB update to SVL for their 138kV rated station equipment. Nippon Paper name change to McKinley Paper Biomass | 2021-01-05 | JW
Cowlitz Fall reference voltage change from POI to Glenoma Benton 115kV band change for Winter to -1 for DSO 134 Updated Cover for distributed generation the threshold for start-up and shutdown to included new requirements from interconnection agreements. Included information on voltage droop and clearified notification requirements. Added Blue Ridge (Wheatridge Wind) to Gen Schedules. Change target for Leaning Juniper to match all other Jones Canyon Plants. Change to Hot Springs Low and Target, historical analysis and AVC reactor settings Changed Bonneville 115 gen reference to Bonneville PH 115 High 115kV schedule lowered to 121 at Boundary, Boardman, Carmen Smith, Hopkins Ridge, and Horn Butte to match continuous high voltage limits. High 138kV schedule lowered to 145 at Minidoka to match continuous high voltage limits. High 230kV schedule lowered to 242 at Arlington wind, Leaning Juniper 1&2, Pebble Springs, Wheatfeild to match continuous high voltage limits. Boardman (PGE) gen removed due to closure of plant. | 2020-11-05 | JW
Added WEYCO 3 (International Paper, EWEB), to gen schedules. Removed Klamath Gen Schedule per PAC request (not BPA TOP or BA). Changed Plant names on Gen schedules: Rattles Snake Road (Horizon) to "Arlington Wind, Rattlesnake Road (EDP)", Carmen Smith (EWEB) to "Carmen Smith, Trail Bridge (EWEB)", Mullan (Tucannon River) to Tucannon River (Mullan, PGE). Ashe 500kV schedule added and Ashe 230kV min voltage increased to 237kV and Benton 115kV voltage winter band reduced to -1 to match DSO 134 values. Change "Station" column title to "Plant" (Gen sch.) Created Target column for Target voltage (Gen Sch.) instead of utilizing the remarks column for this information. Targets added to Flat Gen Sch. Added User Guide Sheet. Added GOP Notification Requirements to Cover. | 2020-05-21 | JW
Annual review and update. Updated contact phone number and email. Updated Intermediate in timetable to Medium to match schedules. Updated cover, holiday, timetable statements and format. Included correlated WECC base case regulated and gen bus numbers to gen schedules tab (hidden). Added Carmen Smith (EWEB) to gen schedules. East Omak 230, Maple Valley 500, Olympia 500, Santiam 500, Tillamook 230, and White Bluffs 230 subs removed (transformer terminated) | 2019-12-20 | JW
Annual review and update, Added River Road Gen. Removed Swift Gen (PAC TOP). | 2018-12-28 | SBH
Revised Boundary, Box Canyon and Coyote Springs Gen schedules, and Boundary, Colville, Coyote Springs and Slatt Substation schedules. | 2018-07-23 | SBH
Revised Horse Heaven and Benton. Added Tin Cup. Added Seasonal Sub Schedule tab. Removed Potholes. Removed Big Hanaford from Gen Schedules. | 2017-12-22 | SBH
Annual review and update, Conkelley change from time-of-day | 2016-12-23 | SBH
Added Grand Coulee 115-kV Gen schedule | 2016-03-15 | SBH
Revised Coulee and Chief Jo 500, revised Priest Rapids & Midway, added Carty, removed Snohomish note | 2016-03-08 | SBH
Annual review and update | 2015-12-29 | SBH
Revised Hopkins Ridge Max, Min & Target. Update for Vantage and Wanapum. | 2015-05-08 | SBH
Annual review and update | 2014-12-24 | SBH
Added substation schedule voltage band and target per VAR-001-4 Req. 1 for 01-OCT-14 enforcement | 2014-09-22 | SBH
Added Mullan (Tucannon) Wind. Removed Grand Coulee 115. Removed some non-BES buses. Revised Redmond. | 2014-09-04 | SBH
Revised Central Ferry and LS Wind sites. | 2014-04-29 | SBH
Edit typo on Coulee 115 reference voltage | 2014-04-29 | SBH
Added to cover page - VAR-002-2b R1 start-up & shutdown mode information for distributed generators | 2014-04-29 | SBH
Added Tolerance Band, voltage reference and TOP adjacency | 2013-12-20 | SBH
Remove Black Canyon, Carmen Smith, River Road, Mayfield, Mossyrock, Merwin, Yale | 2013-12-20 | SBH
Added Packwood | 2013-12-20 | SBH
Added Nippon Paper to GEN Schedules | 2013-09-03 | SBH
Removed Henry Jackson from GEN Schedule | 2013-02-20 | SBH
Revised Central Ferry and LS Wind sites, and annual update to holiday schedule. | 2013-01-02 | SBH
Added Schedule for Kittitas | 2012-08-12 | SBH
Change for Mint Farm minimum voltage | 2012-08-12 | SBH