## WECC Equivalent
Project data input |  |  | Powerflow data |  | Collector system branches |  |  |  | No of WTG |  | 23 |  | Topology for this example
|  |  | Imped. on 100MVA base |  | From | To | R | X | B | n | R n^2 | X n^2
WTG Unit Data |  |  |  |  | T16 | T17 | 0.015887 | 0.0040076 | 0.00016154 | 1 | 0.015887 | 0.0040076
Capacity | 2.1 | MW | Pmax | 48.3 | T17 | T6 | 0.044129 | 0.011132 | 0.00044871 | 2 | 0.17652 | 0.044528
PF(Lag) | 0.9534 |  | Qmax | 14.5726 | T6 | T7 | 0.019417 | 0.0048981 | 0.00019743 | 3 | 0.17475 | 0.044083
PF(Lead) | -0.9534 |  | Qmin | -14.5726 | T7 | T8 | 0.017652 | 0.0044528 | 0.00017949 | 4 | 0.28243 | 0.071246
No. WTGs | 23 |  |  |  | T8 | T9 | 0.019417 | 0.0048981 | 0.00019743 | 5 | 0.48542 | 0.12245
[5 empty] | T9 | T10 | 0.0037807 | 0.0035287 | 0.00029615 | 6 | 0.13611 | 0.12703
Unit Transformer |  |  |  |  | T10 | JB1-2 | 0.0090737 | 0.0084688 | 0.00071076 | 7 | 0.44461 | 0.41497
LV | 0.6 | kV | MVA | 51.75 | T11 | T12 | 0.021182 | 0.0053434 | 0.00021538 | 1 | 0.021182 | 0.0053434
HV | 34.5 | kV | Z | 0.11594 | T12 | T13 | 0.019417 | 0.0048981 | 0.00019743 | 2 | 0.077668 | 0.019593
MVA | 2.25 |  | R | 0.011537 | T13 | JB1-2 | 0.035304 | 0.0089057 | 0.00035897 | 3 | 0.31773 | 0.080151
Z (%) | 6 | on MVA base | X | 0.11537 | JB1-2 | JB1-1 | 0.0068221 | 0.0092586 | 0.0011191 | 10 | 0.68221 | 0.92586
X/R | 10 |  |  |  | T18 | JB1-1 | 0.015887 | 0.0040076 | 0.00016154 | 1 | 0.015887 | 0.0040076
[5 empty] | JB1-1 | SUB | 0.010116 | 0.013728 | 0.0016593 | 11 | 1.224 | 1.6611 | Partial R | Partial X
Station Transformer |  |  |  |  | T5 | T4 | 0.026478 | 0.0066793 | 0.00026923 | 1 | 0.026478 | 0.0066793 | 8.9666 | 8.2356
MVA | 70 | ONAN | MVA | 117 | T4 | T3 | 0.026478 | 0.0066793 | 0.00026923 | 2 | 0.10591 | 0.026717
MVA | 93 | OF | Z | 0.085714 | T3 | T2 | 0.022947 | 0.0057887 | 0.00023333 | 3 | 0.20653 | 0.052098 | Collector System Equivalent Model
MVA | 117 | OFAF | R | 0.01681 | T2 | T1 | 0.014128 | 0.0064524 | 0.00035179 | 4 | 0.22605 | 0.10324 | (Same units as R, X & B data)
Z% | 6 | % ONAN | X | 0.08405 | T1 | T43 | 0.01457 | 0.0066541 | 0.00036279 | 5 | 0.36424 | 0.16635 | R | 0.01695
X/R | 5 |  |  |  | T43 | JB2-2 | 0.0097131 | 0.004436 | 0.00024186 | 6 | 0.34967 | 0.1597 | X | 0.015568
[5 empty] | T34 | JB2-2 | 0.026478 | 0.0066793 | 0.00026923 | 1 | 0.026478 | 0.0066793 | B | 0.012977
Model these explicitly: |  |  |  |  | JB2-2 | JB2-1 | 0.023629 | 0.022054 | 0.0018509 | 7 | 1.1578 | 1.0807
[5 empty] | T14 | T15 | 0.015887 | 0.0040076 | 0.00016154 | 1 | 0.015887 | 0.0040076
Capacitors Mvar |  |  | Statcom/SVC Mvar |  | T15 | T20 | 0.016769 | 0.0042302 | 0.00017051 | 2 | 0.067077 | 0.016921 | Do not change the data and formulas in Pink
At WTG |  |  | Qmin |  | T20 | JB2-1 | 0.010591 | 0.0026717 | 0.00010769 | 3 | 0.095319 | 0.024045
At collector |  |  | Qmax |  | T21 | JB2-1 | 0.015887 | 0.0040076 | 0.00016154 | 1 | 0.015887 | 0.0040076 | Please DO change the input data in Green
[5 empty] | JB2-1 | T19 | 0.0021172 | 0.0028733 | 0.0003473 | 11 | 0.25618 | 0.34767
NOTE |  |  |  |  | T19 | SUB | 0.013879 | 0.018836 | 0.0022768 | 12 | 1.9986 | 2.7124
USE AT YOUR OWN RISK. This is an example with made up data representing a 27 MW wind farm with 18 Type 3 WTGs, 1.5 MW each. Input datea goes in cell shaded Green. Output data are in cells shaded Blue. Do not modify formulas in cells shaded Pink. Contact: | [10 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
If more room is neede, modify equivalent impedance formulas
Note on N3: Abraham Ellis: Nomber of turbines injecting through branch
Note on F5: Abraham Ellis: If Pgen < Pmax, adjust Qmax and Qmin accordingly
Note on C6: Abraham Ellis: At WTG terminals, without pf correction capacitors. Model power factor correction capacitors explicitly
Note on F11: Abraham Ellis: Rating 1 and Rating 2 in powerflow
Note on F18: Abraham Ellis: Rating 1 and Rating 2 in powerflow

## Full Detail Model
Typical Collection System Cable Schedule | [16 empty] | Zbase | 11.9025 | 0.084016
Unit Size |  |  |  | 2.3 | MW
System KV |  |  |  | 34.5 | kV
Peak Amps / phase |  |  |  |  | = MW *1000,000*1/sqrt3 * 1/(Vl-l*1000)
|  |  | 6000 | [14 empty] | Per Unit Calculations
CIRCUIT | FROM | TO | FROM | TO | LENGTH (FT) | CONDUCTOR | IC (uA) | 1/Xc | Positive &Negative |  | Zero Sequence |  | Units This Segment | MW This Segment | Peak Amps | Cable Ultimate Ampacity |  | Positive &Negative |  | 1/Xc
[9 empty] | Real | Reactive | Real | Reactive | [5 empty] | Real | Reactive |  | MODEL BRANCH DATA
1 | T16 | T17 | 6026 | 6024 | 900 | 1/0 AWG | 0 | 1.3572e-05 | 0.18909 | 0.0477 |  |  | 1 | 2.3 | 38.49 | 132 | 7.8878 | 0.015887 | 0.0040076 | 0.00016154 | 6026, 6024 '1 ', 0.01589, 0.00401, 0.00016, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | T17 | T6 | 6024 | 6022 | 2500 | 1/0 AWG | 0 | 3.7699e-05 | 0.52525 | 0.1325 |  |  | 2 | 4.6 | 76.98 | 132 | 7.8878 | 0.044129 | 0.011132 | 0.00044871 | 6024, 6022 '1 ', 0.04413, 0.01113, 0.00045, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | T6 | T7 | 6022 | 6020 | 1100 | 1/0 AWG | 0 | 1.6588e-05 | 0.23111 | 0.0583 |  |  | 3 | 6.9 | 115.4701 | 132 | 7.8878 | 0.019417 | 0.0048981 | 0.00019743 | 6022, 6020 '1 ', 0.01942, 0.0049, 0.0002, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | T7 | T8 | 6020 | 6018 | 1000 | 1/0 AWG | 0 | 1.508e-05 | 0.2101 | 0.053 |  |  | 4 | 9.2 | 153.9601 | 132 | 7.8878 | 0.017652 | 0.0044528 | 0.00017949 | 6020, 6018 '1 ', 0.01765, 0.00445, 0.00018, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | T8 | T9 | 6018 | 6016 | 1100 | 1/0 AWG | 0 | 1.6588e-05 | 0.23111 | 0.0583 |  |  | 5 | 11.5 | 192.4501 | 132 | 7.8878 | 0.019417 | 0.0048981 | 0.00019743 | 6018, 6016 '1 ', 0.01942, 0.0049, 0.0002, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | T9 | T10 | 6016 | 6014 | 1000 | 500 kCMIL | 0 | 2.4881e-05 | 0.045 | 0.042 |  |  | 6 | 13.8 | 230.9401 | 317 | 18.9426 | 0.0037807 | 0.0035287 | 0.00029615 | 6016, 6014 '1 ', 0.00378, 0.00353, 0.0003, 18.94, 18.94, 18.94, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | T10 | JB1-2 | 6014 | 6006 | 2400 | 500 kCMIL | 0 | 5.9715e-05 | 0.108 | 0.1008 |  |  | 7 | 16.1 | 269.4301 | 317 | 18.9426 | 0.0090737 | 0.0084688 | 0.00071076 | 6014, 6006 '1 ', 0.00907, 0.00847, 0.00071, 18.94, 18.94, 18.94, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | T11 | T12 | 6012 | 6010 | 1200 | 1/0 AWG | 0 | 1.8096e-05 | 0.25212 | 0.0636 |  |  | 1 | 2.3 | 38.49 | 132 | 7.8878 | 0.021182 | 0.0053434 | 0.00021538 | 6012, 6010 '1 ', 0.02118, 0.00534, 0.00022, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | T12 | T13 | 6010 | 6008 | 1100 | 1/0 AWG | 0 | 1.6588e-05 | 0.23111 | 0.0583 |  |  | 2 | 4.6 | 76.98 | 132 | 7.8878 | 0.019417 | 0.0048981 | 0.00019743 | 6010, 6008 '1 ', 0.01942, 0.0049, 0.0002, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | T13 | JB1-2 | 6008 | 6006 | 2000 | 1/0 AWG | 0 | 3.0159e-05 | 0.4202 | 0.106 |  |  | 3 | 6.9 | 115.4701 | 132 | 7.8878 | 0.035304 | 0.0089057 | 0.00035897 | 6008, 6006 '1 ', 0.0353, 0.00891, 0.00036, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | JB1-2 | JB1-1 | 6006 | 6002 | 2900 | 1000 Kcmil | 0 | 9.4022e-05 | 0.0812 | 0.1102 |  |  | 10 | 23 | 384.9002 | 425 | 25.3962 | 0.0068221 | 0.0092586 | 0.0011191 | 6006, 6002 '1 ', 0.00682, 0.00926, 0.00112, 25.4, 25.4, 25.4, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | T18 | JB1-1 | 6004 | 6002 | 900 | 1/0 AWG | 0 | 1.3572e-05 | 0.18909 | 0.0477 |  |  | 1 | 2.3 | 38.49 | 132 | 7.8878 | 0.015887 | 0.0040076 | 0.00016154 | 6004, 6002 '1 ', 0.01589, 0.00401, 0.00016, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
1 | JB1-1 | SUB | 6002 | 6000 | 4300 | 1000 Kcmil | 0 | 0.00013941 | 0.1204 | 0.1634 |  |  | 11 | 25.3 | 423.3902 | 425 | 25.3962 | 0.010116 | 0.013728 | 0.0016593 | 6002, 6000 '1 ', 0.01012, 0.01373, 0.00166, 25.4, 25.4, 25.4, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
CIRCUIT | FROM | TO | FROM | TO | LENGTH (FT) | CONDUCTOR | IC (uA) | 1/Xc | Positive &Negative |  | Zero Sequence |  | Units This Segment | MW This Segment | Peak Amps | Cable Ultimate Ampacity |  | Positive &Negative |  | 1/Xc
[9 empty] | Real | Reactive | Real | Reactive | [5 empty] | Real | Reactive
2 | T5 | T4 | 6054 | 6052 | 1500 | 1/0 AWG | 0 | 2.2619e-05 | 0.31515 | 0.0795 | 0 | 0 | 1 | 2.3 | 38.49 | 132 | 7.8878 | 0.026478 | 0.0066793 | 0.00026923 | 6054, 6052 '1 ', 0.02648, 0.00668, 0.00027, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | T4 | T3 | 6052 | 6050 | 1500 | 1/0 AWG | 0 | 2.2619e-05 | 0.31515 | 0.0795 | 0 | 0 | 2 | 4.6 | 76.98 | 132 | 7.8878 | 0.026478 | 0.0066793 | 0.00026923 | 6052, 6050 '1 ', 0.02648, 0.00668, 0.00027, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | T3 | T2 | 6050 | 6048 | 1300 | 1/0 AWG | 0 | 1.9604e-05 | 0.27313 | 0.0689 | 0 | 0 | 3 | 6.9 | 115.4701 | 132 | 7.8878 | 0.022947 | 0.0057887 | 0.00023333 | 6050, 6048 '1 ', 0.02295, 0.00579, 0.00023, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | T2 | T1 | 6048 | 6046 | 1600 | 4/0 AWG | 0 | 2.9556e-05 | 0.16816 | 0.0768 | 0 | 0 | 4 | 9.2 | 153.9601 | 197 | 11.7719 | 0.014128 | 0.0064524 | 0.00035179 | 6048, 6046 '1 ', 0.01413, 0.00645, 0.00035, 11.77, 11.77, 11.77, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | T1 | T43 | 6046 | 6044 | 1650 | 4/0 AWG | 0 | 3.048e-05 | 0.17341 | 0.0792 | 0 | 0 | 5 | 11.5 | 192.4501 | 197 | 11.7719 | 0.01457 | 0.0066541 | 0.00036279 | 6046, 6044 '1 ', 0.01457, 0.00665, 0.00036, 11.77, 11.77, 11.77, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | T43 | JB2-2 | 6044 | 6040 | 1100 | 4/0 AWG | 0 | 2.032e-05 | 0.11561 | 0.0528 | 0 | 0 | 6 | 13.8 | 230.9401 | 197 | 11.7719 | 0.0097131 | 0.004436 | 0.00024186 | 6044, 6040 '1 ', 0.00971, 0.00444, 0.00024, 11.77, 11.77, 11.77, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | T34 | JB2-2 | 6042 | 6040 | 1500 | 1/0 AWG | 0 | 2.2619e-05 | 0.31515 | 0.0795 | 0 | 0 | 1 | 2.3 | 38.49 | 132 | 7.8878 | 0.026478 | 0.0066793 | 0.00026923 | 6042, 6040 '1 ', 0.02648, 0.00668, 0.00027, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | JB2-2 | JB2-1 | 6040 | 6030 | 6250 | 500 kCMIL | 0 | 0.00015551 | 0.28125 | 0.2625 | 0 | 0 | 7 | 16.1 | 269.4301 | 317 | 18.9426 | 0.023629 | 0.022054 | 0.0018509 | 6040, 6030 '1 ', 0.02363, 0.02205, 0.00185, 18.94, 18.94, 18.94, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | T14 | T15 | 6038 | 6036 | 900 | 1/0 AWG | 0 | 1.3572e-05 | 0.18909 | 0.0477 | 0 | 0 | 1 | 2.3 | 38.49 | 132 | 7.8878 | 0.015887 | 0.0040076 | 0.00016154 | 6038, 6036 '1 ', 0.01589, 0.00401, 0.00016, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | T15 | T20 | 6036 | 6034 | 950 | 1/0 AWG | 0 | 1.4326e-05 | 0.19959 | 0.05035 | 0 | 0 | 2 | 4.6 | 76.98 | 132 | 7.8878 | 0.016769 | 0.0042302 | 0.00017051 | 6036, 6034 '1 ', 0.01677, 0.00423, 0.00017, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | T20 | JB2-1 | 6034 | 6030 | 600 | 1/0 AWG | 0 | 9.0478e-06 | 0.12606 | 0.0318 | 0 | 0 | 3 | 6.9 | 115.4701 | 132 | 7.8878 | 0.010591 | 0.0026717 | 0.00010769 | 6034, 6030 '1 ', 0.01059, 0.00267, 0.00011, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | T21 | JB2-1 | 6032 | 6030 | 900 | 1/0 AWG | 0 | 1.3572e-05 | 0.18909 | 0.0477 | 0 | 0 | 1 | 2.3 | 38.49 | 132 | 7.8878 | 0.015887 | 0.0040076 | 0.00016154 | 6032, 6030 '1 ', 0.01589, 0.00401, 0.00016, 7.89, 7.89, 7.89, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | JB2-1 | T19 | 6030 | 6028 | 900 | 1000 Kcmil | 0 | 2.9179e-05 | 0.0252 | 0.0342 | 0 | 0 | 11 | 25.3 | 423.3902 | 425 | 25.3962 | 0.0021172 | 0.0028733 | 0.0003473 | 6030, 6028 '1 ', 0.00212, 0.00287, 0.00035, 25.4, 25.4, 25.4, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
2 | T19 | SUB | 6028 | 6000 | 5900 | 1000 Kcmil | 0 | 0.00019129 | 0.1652 | 0.2242 | 0 | 0 | 12 | 27.6 | 461.8802 | 425 | 25.3962 | 0.013879 | 0.018836 | 0.0022768 | 6028, 6000 '1 ', 0.01388, 0.01884, 0.00228, 25.4, 25.4, 25.4, 0.00000, 0.00000, 0.00000, 0.00000,1, 0.00, 1,1.0000
Sub 2

## Cable Data
Conductor Data
Per 1000 ft Values
CONDUCTOR | IC (uA) | Xc (Meg_ohm/ft) | Positive &Negative |  | Zero Sequence
|  |  | Real | Reactive | Real | Reactive | Ampacity
1/0 AWG |  | 66314559.62 | 0.2101 | 0.053 |  |  | 132
4/0 AWG |  | 54134334.38 | 0.1051 | 0.048 |  |  | 197
350KCMIL |  | 50048724.24 | 0.066 | 0.045 |  |  | 400
500 kCMIL |  | 40190642.19 | 0.045 | 0.042 |  |  | 317
750kCMIL |  | 38443222.97 | 0.034 | 0.039 |  |  | 640
1000 kCMIL |  | 30843981 | 0.028 | 0.038 |  |  | 425
1250 kCMIL |  | 31578361.72 | 0.019 | 0.07 |  |  | 830